Structured Network Cabling CIS 399 Day 1, Morning Session 2
Structured Network Cabling
CIS 399
Day 1, Morning Session 2
Dale Smith
University of Oregon & NSRC
dsmith@uoregon.edu

---
We all have some ugly wiring
We all have some ugly wiring

---
Structured Cabling Systems
Structured Cabling Systems
Only two types of cabling:
  - Unshielded twisted pair copper – provides service to individual computers and between network closets
  - Fiber optic cabling – provides service to buildings and between network closets
Everything is run in a star configuration
Data closet
Core Location
cat5e
Fiber optic

---
Unshielded Twisted Pair Cable
Unshielded Twisted Pair Cable
- Run in star configuration from Network Closet location to individual outlets in offices or labs.
- Run at least two cables to every outlet – I recommend four if you can afford it.
- Run at least six cables between network closets if the distance is less than 90 meters
- Question: what type of cable to run? Cat5, cat5e, Cat6, ???

---
What type of UTP
What type of UTP
What speed does each type support?
Cable Type	Max Speed	Max Distance	Cost Factor
Category 5	100Mbs	100m	1x
Category 5e	1000Mbs	100m	1x
Category 6	1000Mbs	100m	1.3x
Category 6	10,000Mbs	57m	1.3x
Category 6a	10,000Mbs	100m	2x
Strongly recommend category 5e cabling.

---
Unshielded Twisted Pair Cable
Labeling is a key to reduce work later

---
Fiber Optic Cabling
Fiber Optic Cabling
Two basic types of fiber
  - Multi Mode limited to 2km @ 100Mbs
  - Single Mode 70km @ virtually unlimited
Multiple types of multi mode
  - 62.5 micron core
  - 50 micron core
Multiple types of single mode
  - Optimized for 1310 and 1550 nm operation
  - Optimized for WDM operation

---
Physics of Fiber
Physics of Fiber

---
What type of Fiber?
What type of Fiber?
Multi mode Fiber
  - 62.5 micron
    - 100baseFX for 2km, optical interface cost $250 USD
    - 1000baseSX for 275m, optical interface cost $250 USD
    - 1000baseLX for 500m, optical interface cost $750 USD
    - 10GbaseSR for 33m, optical interface cost $2000 USD
    - 10GbaseLRM for 220m, optical interface cost $1500 USD (not widely avail)
  - 50 micron laser optimized
    - 100baseFX for 2km, optical interface cost $250 USD
    - 1000baseSX for 550m, optical interface cost $250 USD
    - 1000baseLX for 500m, optical interface cost $750 USD
    - 10GbaseSR for 300m, optical interface cost $2000 USD
    - 10GbaseLRM for 220m, optical interface cost $1500 USD (not widely avail)
Single mode Fiber
  - 100baseFX not supported
  - 1000baseSX not supported
  - 1000baseLX for 5km (most vendors support 10km), cost $750 USD
  - 1000baseLH (not a standard) 70 km with 1550nm lasers, cost $3000 USD
  - 10GbaseLR for 10km, optical interface cost $3000 USD
  - 10GbaseER for 30-40km, optical interface cost $8500 USD

---
Going Fast on Fiber
Going Fast on Fiber
Multi mode Fiber
  - 62.5 micron
    - 1Gbs to 500m
    - 10Gbs to 220m
  - 50 micron laser optimized
    - 1Gbs to 500m
    - 10Gbs to 300m
Single mode Fiber
  - 1Gbs to 70km
  - 10Gbs to 70km

---
How About Going Even Faster?
How About Going Even Faster?
- Dispersion becomes your enemy at 10Gbs and above (40 and 100Gbs very hard)
- Even single mode fiber has dispersion
  - Chromatic Dispersion (CD) Even slightly different colors of light travel different speeds
  - Polarization Mode Dispersion (PMD) Slight variations from true roundness causes differently polarized light to travel different distances.

---
The Solution Today is WDM
The Solution Today is WDM
Wave Division Multiplexing (WDM)
  - Provisioning multiple Gigabit or 10 Gigabit using different colors of light
  - Coarse (CWDM)
    - Fewer waves, low cost
    - 1310nm frequency spectrum
    - Not suitable for amplification – short haul (70km)
  - Dense (DWDM) more waves
    - More waves, higher cost
    - 1550nm frequency spectrum
    - Suitable for EDFA amplification – long haul (1000s of km)

---
WDM Simple Single Span
WDM Simple Single Span
Single Fiber
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Single Fiber
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter

---
Optical Add Drop Multiplexor
Optical Add Drop Multiplexor
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver
Transmitter
Receiver

---
Can Build Complex Networks
Can Build Complex Networks
Fiber
Pair
Fiber
Pair
Fiber
Pair
OADM
OADM
OADM
OADM
University
University
University
NREN

---
Varying Service Models
Varying Service Models
- Internet Service Provider (ISP) provides Internet and circuit to your site
- ISP is different from provider of circuits
- Best situation when you have choices in both ISP and provider of telecom or fiber services
  - Competition is the key

---
Fiber Optic Topology
Fiber Optic Topology
Fiber Types
  - Multi mode: don’t bother if run is over 200M
  - Single mode: use fiber optimized for 1310/1550nm
- Run in star configuration from core network location to individual buildings
- Also run in star configuration inside of buildings from main phone closet to other closets
- To reduce costs, can run large fiber cable from core to some remote location, then smaller cables from there to surrounding buildings

---
Star Configuration
Star Configuration
Plan for future -- Install enough fiber
  - Minimum: 6 multimode plus 6 single mode from core to each building
  - Minimum: 6 multimode plus 6 single mode from building entrance network closet to every other network closet in the building.
Building to be served
Core network location
Nearby buildings

---
Fiber Optic Topology
Building 1
Network Core Location
fiber
Network Closet 1
fiber
Network Closet 2
fiber
fiber
fiber
fiber
Building 2
Network Closet 3
Building 3
Building 4
fiber
Building 5

---
Construction Hints
Construction Hints
Use outdoor cable between buildings
  - Armored (to protect against rodents)
  - Loose tube
Use indoor cabling inside buildings
  - tight buffer
Standardize on Connectors
  - Multi mode: ST or SC (epoxy or hot melt)
  - Single mode: SC or LC (fusion splice factory pigtails, however hand polish is OK if done properly)

---
Fiber Optic Cable Construction
Fiber Optic Cable Construction
Fiber has bend radius issues

---
More Construction Hints
More Construction Hints
For cable installed in underground conduit:
  - No more than 200m between pull points
  - Reduce distance by 50m for every 90 degrees of bend

---
Fiber Optic Cable Construction
Leave slack loops

---
Putting it all Together
Putting it all Together
Building 1
Network Core Location
fiber
cat5e
Network Closet 1
Cat5e + fiber
Network Closet 2
Cat5e + fiber
fiber
fiber
fiber
Building 2
Network Closet 3
Building 3
cat5e
Building 4
fiber
Building 5

---
Structured Cabling Summary
Structured Cabling Summary
- Install cabling in star configuration – don’t daisy chain
- Install cat5e or cat6a – cat6 is a waste of money if the runs are over 57m
- If runs are under 200M, then multi mode is OK
- Must do single mode if runs over 200M

---
Thank You
Thank You
Questions